## Table3.5_Register
Sym | Group | Design variable (unit) | n | Baseline (L0) | Discrete levels | Realization | ECF source | Sim¹ | Opt²
P1 | Opaque envelope | Wall U-value (W/m²·K) | 5 | 1.073 | {1.07, 0.64, 0.46, 0.36, 0.29} | EPS ETICS 0/25/50/75/100 mm | EC1 | ✓ | ✓
P2 | Opaque envelope | Roof U-value (W/m²·K) | 5 | 0.221 | {0.22, 0.19, 0.17, 0.16, 0.14} | EPS board 0/25/50/75/100 mm | EC1 | ✓ | ✓
P3 | Cool roof | Solar reflectance (–) | 4 | 0.55 | {0.55, 0.63, 0.70, 0.77} | Reflective coating (a = 1−ρ) | EC2 | ✓ | ✓
P4 | Glazing envelope | Glazing U & SHGC (paired) | 5 | U 2.862 / SHGC 0.219 / VT 0.241 | SHGC {0.219,0.19,0.17,0.15,0.13}; U {2.86,1.60,1.50,1.50,1.50}; VT {0.241,0.27,0.24,0.20,0.17} | Spectrally-selective IGU (paired U·SHGC·VT), double argon | EC7 | ✓ | ✓
P5 | Active – HVAC | DX cooling COP (–) | 5 | 3.4 | {3.40, 3.65, 3.90, 4.15, 4.40} | Air-cooled packaged DX swap; gross COP (EER 10.1→13.1) | n/a | ✓ | ✓
P6 | Active – HVAC | Cooling setpoint (°C) | 5 | 24 | {24.0, 24.5, 25.0, 25.5, 26.0} | Occupied cooling setpoint schedule | n/a | ✓ | ✓
P7 | Active – lighting | LPD (W/m²) | 5 | 6.66 | {6.66, 6.0, 5.3, 4.6, 4.0} | LED panel retrofit (efficacy-driven) | EC3 | ✓ | ✓
P8 | Renewable | Rooftop PV (kWp) | 6 | 0 | {0, 30, 60, 90, 120, 150} | Roof mono-Si array; PVWatts post-proc (tilt 10°/az 180°) | EC4 | ✗ | ✓
P9 | Storage | BESS (kWh) | 6 | 0 | {0, 30, 60, 90, 120, 150} | LFP BESS; rule-based self-consumption (zero-export) | EC5 | ✗ | ✓
Note on H2: ECF source IDs trỏ sheet DataSources (EC1 = ITB EPD 148/2021).

## LevelInventory
Param | Level | Design value | Realization detail | jEPlus control | A1–A3 (kgCO₂e/m² floor) | B4 (kgCO₂e/m² floor) | Capital cost (USD/m² floor) | EC source | Cost source | Notes
P1 | L0 | 1.073 | EPS 0 mm (baseline wall) | wall_P1_L0 | 0 | 0 | 0 | baseline | — | No-intervention rung
P1 | L1 | 0.642 | EPS 25 mm | wall_P1_L1 | 0.361 | 0 | 10–17 | EC1 | C10 | ETICS proxy (VN thin); P1 expected inactive
P1 | L2 | 0.458 | EPS 50 mm | wall_P1_L2 | 0.722 | 0 | 11–18 | EC1 | C10
P1 | L3 | 0.356 | EPS 75 mm | wall_P1_L3 | 1.083 | 0 | 12–19 | EC1 | C10
P1 | L4 | 0.291 | EPS 100 mm | wall_P1_L4 | 1.444 | 0 | 13–20 | EC1 | C10
P2 | L0 | 0.221 | EPS 0 mm (baseline roof) | roof_P2_L0 | 0 | 0 | 0 | baseline | — | No-intervention rung; U with film
P2 | L1 | 0.194 | EPS 25 mm | roof_P2_L1 | 0.453 | 0 | 0.45–0.77 | EC1 | C1 | material-only
P2 | L2 | 0.173 | EPS 50 mm | roof_P2_L2 | 0.905 | 0 | 0.90–1.54 | EC1 | C1
P2 | L3 | 0.156 | EPS 75 mm | roof_P2_L3 | 1.358 | 0 | 1.35–2.31 | EC1 | C1
P2 | L4 | 0.143 | EPS 100 mm | roof_P2_L4 | 1.81 | 0 | 1.80–3.08 | EC1 | C1
P3 | L0 | 0.55 | No coating (a=0.45) | F13 Abs:Solar=0.45 | 0 | 0 | 0 | baseline | — | No-intervention rung; = ASHRAE 90.1-19 CZ0-3 min aged (SR0.55/TE0.75)
P3 | L1 | 0.63 | Cool coating (a=0.37) | F13 Abs:Solar=0.37 | 0.49 | 0 | 1.7–2.7 | EC2 | C3 | aged 3-yr SR = Title 24 min; material-only; TE giữ 0.75
P3 | L2 | 0.7 | HP white acrylic (a=0.30) | F13 Abs:Solar=0.30 | 0.49 | 0 | 1.7–2.7 | EC2 | C3 | aged trong dải CRRC 0.62–0.77
P3 | L3 | 0.77 | Premium white (a=0.23) | F13 Abs:Solar=0.23 | 0.49 | 0 | 1.7–2.7 | EC2 | C3 | DOE Cool Roof Guide: 0.87→0.77 aged
P4 | L0 | U=2.862; SHGC=0.219; VT=0.241 | Baseline IGU (verified IDF+table.htm); keep existing | P4: 12 fields E/S/W/N×U/SHGC/VT (untouched); WWR & frame fixed | 0 | 0 | 0 | baseline | — | No-intervention rung; 13 Daylighting:Controls → VT affects f1
P4 | L1 | U=1.60; SHGC=0.19; VT=0.27 | Double spectrally-selective low-e, argon (mid solar-control) | P4 tag → 12 fields =1.60/0.19/0.27 | 3.9 | 0 | 8–14 | EC7 | C9 | Framing A (full reglaze, L0=$0); A1–A3=full new IGU; U↓ near-inactive in Aw
P4 | L2 | U=1.50; SHGC=0.17; VT=0.24 | Double SS low-e argon — AGC solar-control floor (g0.17/Tv0.24/Ug≤1.1) | P4 tag → 12 fields =1.50/0.17/0.24 | 3.9 | 0 | 9–14 | EC7 | C9 | Anchor = real AGC documented edge
P4 | L3 | U=1.50; SHGC=0.15; VT=0.20 | Tinted spectrally-selective, argon | P4 tag → 12 fields =1.50/0.15/0.20 | 3.9 | 0 | 11–16 | EC7 | C9 | SHGC↓ but VT↓ → daylight trade-off begins to bite
P4 | L4 | U=1.50; SHGC=0.13; VT=0.17 | Reflective/heavy-tint selective, argon (best solar control) | P4 tag → 12 fields =1.50/0.13/0.17 | 3.9 | 0 | 13–19 | EC7 | C9 | Below AGC std floor (specialty); lowest VT; cap at L3 if conservative
P5 | L0 | 3.4 | Air-cooled packaged DX, baseline (gross COP; EER 10.1; AHRI 340/360 ≥240k) | Baseline untouched =3.3993; 6 fields bot/mid/top×hi/lo | 0 | 0 | 0 | n/a (scope) | — | No-intervention rung; L0=90.1-2019 ≥240k min; A1–A3=0 = SCOPE boundary (no COP-resolved EPD), not physical 0
P5 | L1 | 3.65 | Packaged DX swap, EER~10.8 (code-typical ~90.1-2010 min) | P5 tag → 6 fields =3.65; cap/airflow AUTOSIZE fixed | 0 | 0 | 38–53 | n/a (scope) | C8 | Framing A (full-unit swap, L0=$0). Cost/carbon asymmetry justified (diff. citability + negligible + common-mode)
P5 | L2 | 3.9 | Packaged DX swap, EER~11.6 (high-eff, AAON entry 12.1) | P5 tag → 6 fields =3.90; cap/airflow AUTOSIZE fixed | 0 | 0 | 41–58 | n/a (scope) | C8 | +~10% premium vs L1 base
P5 | L3 | 4.15 | Packaged DX swap, EER~12.3 (CEE Adv. Tier very-large) | P5 tag → 6 fields =4.15; cap/airflow AUTOSIZE fixed | 0 | 0 | 45–63 | n/a (scope) | C8 | +~20% premium
P5 | L4 | 4.4 | Packaged DX swap, EER~13.1 (premium best-available air-cooled) | P5 tag → 6 fields =4.40; cap/airflow AUTOSIZE fixed | 0 | 0 | 49–69 | n/a (scope) | C8 | Ceiling per AAON 12.1–14.8; hạ về 4.20 nếu bảo thủ. DX life ~15y → L0 B4-cost (yr15 in-kind) trong LCC engine
P6 | L0 | 24 | Occupied SP 24.0°C (baseline) | CLGSETP occ=24.0 | 0 | 0 | 0 | n/a | — | No-intervention rung; setback 26.7 fixed; PMV≈−0.3 (hơi mát)
P6 | L1 | 24.5 | Occupied SP 24.5°C | CLGSETP occ=24.5 | 0 | 0 | 0 | n/a | — | operational-only
P6 | L2 | 25 | Occupied SP 25.0°C | CLGSETP occ=25.0 | 0 | 0 | 0 | n/a | — | operational-only
P6 | L3 | 25.5 | Occupied SP 25.5°C | CLGSETP occ=25.5 | 0 | 0 | 0 | n/a | — | operational-only
P6 | L4 | 26 | Occupied SP 26.0°C | CLGSETP occ=26.0 | 0 | 0 | 0 | n/a | — | Comfort edge; g1 ¦PMV¦≤0.5 binds (0.5clo/0.2m·s⁻¹)
P7 | L0 | 6.66 | Baseline luminaires (no intervention) | Lights W/m² ×15 = 6.66362 | 0 | 0 | 0 | baseline | — | No-intervention rung; QCVN LPD≤11 non-binding
P7 | L1 | 6 | LED panel 600×600, illuminance-preserved | Lights W/m² ×15 = 6.0 | 8.3 | 0 | 3.2–6.1 | EC3 | C4 | material-only; efficacy-driven
P7 | L2 | 5.3 | LED panel 600×600, illuminance-preserved | Lights W/m² ×15 = 5.3 | 8.3 | 0 | 3.2–6.1 | EC3 | C4 | material-only
P7 | L3 | 4.6 | LED panel 600×600, illuminance-preserved | Lights W/m² ×15 = 4.6 | 8.3 | 0 | 3.2–6.1 | EC3 | C4 | material-only
P7 | L4 | 4 | High-efficacy LED ~165–170 lm/W | Lights W/m² ×15 = 4.0 | 8.3 | 0 | 3.2–6.1 | EC3 | C4 | material-only; floor = current panel efficacy
P8 | L0 | 0 kWp | No PV (baseline roof) | Post-proc: 0 kWp (no PV); not in jEPlus | 0 | 0 | 0 | baseline | — | No-intervention rung; f1/EUI demand-side → PV never affects f1
P8 | L1 | 30 kWp (6.02 W/m²flr) | Roof mono-Si ~143 m² mod / ~204 m² footprint (12% roof) | Post-proc: PVgen = SY×kWp (SY via PVWatts tilt10°/az180°/loss14%) | 3.7 | 0.21 | 2.3–3.0 | EC4 | C6 | A1–A3=615 kgCO₂e/kWp (system, Louwen2016/Etude2025). B4=inverter ×1 @~yr12. PV→f2,f3
P8 | L2 | 60 kWp (12.04 W/m²flr) | Roof mono-Si ~286 m² mod / ~408 m² footprint (25% roof) | Post-proc: PVgen = SY×kWp | 7.41 | 0.42 | 4.6–6.0 | EC4 | C6 | Daytime office → high self-consumption (f2)
P8 | L3 | 90 kWp (18.06 W/m²flr) | Roof mono-Si ~429 m² mod / ~612 m² footprint (37% roof) | Post-proc: PVgen = SY×kWp | 11.11 | 0.63 | 7.0–9.0 | EC4 | C6
P8 | L4 | 120 kWp (24.09 W/m²flr) | Roof mono-Si ~571 m² mod / ~816 m² footprint (49% roof) | Post-proc: PVgen = SY×kWp | 14.81 | 0.84 | 9.3–12.0 | EC4 | C6 | ≥100 kW → NĐ58/2025 registration (S8); affects f2 export
P8 | L5 | 150 kWp (30.11 W/m²flr) | Roof mono-Si ~714 m² mod / ~1020 m² footprint (61% roof; feasibility edge) | Post-proc: PVgen = SY×kWp | 18.52 | 1.05 | 11.6–15.1 | EC4 | C6 | Near practical roof max. 20yr B6 offset ≈564 ≫ embodied 19.6 kgCO₂e/m² → f3 net −544
P9 | L0 | 0 kWh | No BESS (baseline) | Post-proc: 0 kWh (no storage); not in jEPlus | 0 | 0 | 0 | baseline | — | No-intervention rung; f1/EUI unchanged (BESS only time-shifts)
P9 | L1 | 30 kWh (6.02 Wh/m²flr) | LFP pack ~27 kWh usable (DoD 90%) + BMS; hybrid-coupled | Post-proc: dispatch on PV+load; RTE 90%, zero grid-charge, zero-export | 0.42 | 0.42 | 1.6–2.5 | EC5 | C7 | A1–A3=70 kgCO₂e/kWh (LFP, Degen 2024). B4=1 replacement (~6000 cyc/10–15y). BESS→f2,f3
P9 | L2 | 60 kWh (12.04 Wh/m²flr) | LFP ~54 kWh usable + BMS | Post-proc: dispatch; RTE 90%, zero-export | 0.84 | 0.84 | 3.2–5.1 | EC5 | C7 | Recovers clipped PV only → daytime office: small uplift (secondary paradox)
P9 | L3 | 90 kWh (18.06 Wh/m²flr) | LFP ~81 kWh usable + BMS | Post-proc: dispatch; RTE 90%, zero-export | 1.26 | 1.26 | 4.9–7.6 | EC5 | C7
P9 | L4 | 120 kWh (24.09 Wh/m²flr) | LFP ~108 kWh usable + BMS | Post-proc: dispatch; RTE 90%, zero-export | 1.69 | 1.69 | 6.5–10.2 | EC5 | C7 | NSGA-III picks (PV,BESS) independently — not forced 1:1
P9 | L5 | 150 kWh (30.11 Wh/m²flr) | LFP ~135 kWh usable + BMS | Post-proc: dispatch; RTE 90%, zero-export | 2.11 | 2.11 | 8.1–12.7 | EC5 | C7 | Embodied A1–A3+B4=4.22 kgCO₂e/m² fixed → must pay back via recovered PV
Note on F1: A1–A3 incremental vs L0, chuẩn hóa /m² sàn (A_floor=4982 m²). P2: thickness(m) × roof_area(1660.73) × 54.3 kgCO₂e/m³ ÷ 4982. Nguồn ECF: EC1 (ITB EPD 148/2021).
Note on G1: B4 = embodied × số lần thay trong 20 năm. EPS RSL 75 năm → B4=0.
Note on H1: USD/m² sàn, material-only, tỷ giá giả định 26.000 VNĐ/USD (cập nhật khi viết). Installed ≈ ×2.

## DataSources
ID | Type | Description | Value / clause | Source / EPD no. | Publisher | Date | Valid until | Accessed | URL | Used by
EC1 | EPD | EPS board (A1–A3, λ) | 54.3 kgCO₂e/m³; λ 0.040 W/m·K | EPD No. 148/2021 (EN 15804 Type III) | ITB (PL) | 2021 | ⚠ ~2026 VERIFY |  | (dán link/DOI nội bộ) | P1, P2
EC-F1 | EC-Fallback | ICE Database v4.1 | cradle-to-gate A1–A3, EN 15804+A2 | ICE Database | Circular Ecology | 2025 |  | 29/06/2026 | circularecology.com/embodied-carbon-footprint-database.html | fallback (all)
EC-F2 | EC-Fallback | EPS EPD US/Canada industry avg | A1–A3; RSL 75 yr → B4=0 | SIPS 101.1 | SIPS | 2021 |  | 29/06/2026 | sips.org/documents/101.1_EPD_EPS-Insulation.pdf | cross-check EPS
EC-F3 | EC-Fallback | EPS EPD EUMEPS (30 kg/m³) | A1–A3 EN 15804 | EUMEPS (via GLAD) | EUMEPS |  |  | 29/06/2026 | globallcadataaccess.org/expanded-polystyrene-eps-foam-insulation-eumeps-a1-a3-pre-foaming-conditioning-block-moulding-2 | cross-check EPS
C1 | Cost | EPS board trần 50mm | 70.000–120.000 VNĐ/m² | Tân Phú Minh | Tân Phú Minh | 06/2024 |  | 29/06/2026 | tanphuminhcorp.com/tin-tuc/bao-gia-xop-cach-nhiet-day-5cm.html | P2
C2 | Cost | EPS board trần (theo độ dày/tỷ trọng) | 100.000–250.000 VNĐ/m² | Tôn Pu Cách Nhiệt Thế Long | tonpucachnhiet.vn | 03/2026 |  | 29/06/2026 | tonpucachnhiet.vn/tam-cach-nhiet-eps | P2
S1 | Standard | QCVN 09:2017/BXD | roof R0,min≥1.00 (U≤1.00); wall R0≥0.56; OTTVM≤25 W/m²; SHGC theo WWR (B2.1); λ (Phụ lục) | QCVN 09:2017/BXD | Bộ Xây dựng | 2017 |  |  | (project file) | g2, P1–P4
S2 | Standard | LEED v5 BD+C | MRp2 (định lượng A1–A3 bắt buộc); MRc2 (tín chỉ giảm GWP) | LEED v5 BD+C Rating System | USGBC | 2025 |  |  | (project file) | §1.4, benchmarking
S3 | Standard | HD LCA cho SP VLXD | TCVN 14044:2006/ISO 14044; ranh giới A1–A3; LCIA = CML 1992 | Hướng dẫn LCA VLXD | (VN) |  |  |  | (project file) | f3 methodology
S4 | Standard | MONRE Công văn 1726/2024 | EF_grid = 0.6592 kgCO₂e/kWh (dữ liệu 2023) | Công văn 1726/2024 | Bộ TN&MT | 2024 |  |  |  | f3-B6
B1 | Model | IDF prototype | U_wall, U_roof, SHGC 0.219, DX COP 3.40, LPD 6.66, occ 18.58 | ASHRAE901_OfficeMedium_STD2019_HoChiMinh.idf | DOE/PNNL |  |  |  | (project file) | P1–P7, FixedParams
B2 | Model | E+ Envelope Summary | U-factor with/no film (roof 0.221/0.228); refl 0.55; roof 1660.73 m²; floor 4982 m² | ..._table.htm | EnergyPlus |  |  |  | (project file) | L0 envelope
B3 | Model | PNNL Prototype Scorecard | đối chiếu thông số prototype | PNNL_Prototype_Scorecards_MediumOffice_HCMC.xlsx | PNNL |  |  |  | (project file) | §3.1
B4 | Model | CMIP6-VN climate | ACCESS-CM2 + MRI-ESM2-0; SSP245/585; 2050s/2080s; delta-morphing | Tran-Anh et al. 2023 | — | 2023 |  |  |  | §3.2
EC2 | EPD | White acrylic elastomeric roof coating (A1–A3) | 1.46 kgCO₂e/m²·20y (Stage-1, white finish 41-300); RSL 15y (ASTM D6083) | EPD10818 (ISO 21930 Type III) | Sherwin-Williams / NSF | 2023-12-04 | ~04/2028 | 29/06/2026 | info.nsf.org/Certified/Sustain/ProdCert/EPD10818.pdf | P3
EC-F4 | EC-Fallback | GAF Acrylic Top Coat (cross-check) | FU 1m²·20y; RSL 15y | EPD10918 (ISO 21930 Type III) | GAF / NSF | 2024-01-01 | ~01/2029 | 29/06/2026 | gaf.com/.../gaf-acrylic-top-coat-epd.pdf | cross-check P3
C3 | Cost | Sơn chống nóng phản quang KOVA CN-05 | 5.219.000đ/thùng 20kg = 260.950 đ/kg (material) | Paintmart (paintmart.vn) | Thành Vạn Phát | (web listing) | — | 29/06/2026 | paintmart.vn/son-ngoai-that-chong-nong-mai-ton-kova-cn-05-thung-20kg | P3
S5 | Standard | ASHRAE 90.1-2019 §5.5.3.1.1 (roof SR/TE) | CZ0-3: aged SR≥0.55 & TE≥0.75 hoặc SRI≥64 | ASHRAE 90.1-2019 / CRRC S100 | ASHRAE | 2019 | — | 29/06/2026 | ashrae.org (addendum s) | P3 L0 + TE
S6 | Standard | Cool roof ladder anchors (aged 3-yr SR) | Title 24 aged SR≥0.63 (L1); CRRC directory aged SR/product (L2,L3) | Title 24 Part 6 / CRRC Rated Products Directory | CEC / CRRC | 2026 | — | 29/06/2026 | coolroofs.org/directory/roof | P3 ladder
S7 | Standard | ASHRAE 55 / Fanger PMV (cơ sở g1) | ¦PMV¦≤0.5; inputs: 0.5 clo (occupied), 0.2 m/s air, ~1.0–1.2 met | ASHRAE 55 / IDF FANGER model | ASHRAE | 2017 |  | 29/06/2026 | (project file IDF) | g1, P6
EC3 | EPD | LED panel 595×595, 22/29W, 170 lm/W, 1.96 kg | 45.9 kgCO₂e/unit (A1–A3, 29W); power-invariant; L70 100.000h | EPD Hub HUB-5969 (One Click LCA) | OPPLE / EPD Hub | 2026-04-01 | 2031-04-01 | 29/06/2026 | manage.epdhub.com (HUB-5969) | P7
C4 | Cost | LED panel 600×600 36–48W (office grade) | 458k–888k VNĐ/đèn; đại diện ~650k (material) | haledco.com bảng giá | HALEDCO | 2026-01-01 | — | 29/06/2026 | haledco.com/.../bao-gia-den-led-panel-600x600 | P7
C5 | Cost | LED panel 600×600 (cross-check) | Paragon 732k–1.625k; Panasonic 900k–1.280k VNĐ/đèn | dmtlight.vn bảng giá | DMT Light | 2026-04-01 | — | 29/06/2026 | dmtlight.vn/.../bang-gia-den-led-am-tran-600x600 | cross-check P7
B5 | Model | LED retrofit EC/cost model | N=0.18 đèn/m² (≈6.66÷36W; grid 600×600); A1–A3/m² flat=8.3; B4=0 (L70≫20y); floor 4.0=~165 lm/W | Internal (lumen + EC3/B1) | — | — | — | 29/06/2026 | — | P7
EC4 | LCA (peer-rev.) | PV system embodied (c-Si, installed) | 615 kgCO₂e/kWp (2020 ref); sensitivity 400–2,500 (ultra-low ↔ legacy) | Louwen et al. 2016, Nature Energy (via Etude 2025 synthesis) | Louwen et al. / Etude | 2016/2025 | — | 30/06/2026 | etude.co.uk/how-we-work/low-embodied-carbon-of-pv ; doi:10.1038/nenergy.2016.36 | P8
EC6 | Estimate (lit.) | PV inverter embodied → B4 (×1 replacement) | ≈35 kgCO₂e/kWp (~5% system; RSL~12y → 1× in 20y; minor =1.05/m² @150kWp) | Inverter share of WLC profile (CIBSE Marsland 2023); refine w/ inverter EPD | CIBSE / internal | 2023 | — | 30/06/2026 | cibse.org/media/251diyyp/...pv-payback...pdf | P8 (B4)
EC-F5 | EC-Fallback | Brand module EPD cross-check | Trina Vertex N 13.2 gCO₂e/kWh; Jinko, JA Solar (EN15804/ISO14025) — corroborate EC4 | UL Solutions / EPDItaly (Trina); EPEAT 630–857 kgCO₂e/kWp | UL / EPDItaly / GEC | 2021–2025 | — | 30/06/2026 | pveurope.eu (Trina Vertex N EPD); globalelectronicscouncil.org | cross-check P8
C6 | Cost | Rooftop PV turnkey, grid-tied (commercial 30–150 kWp, no BESS) | 10–15 tr VNĐ/kWp (comm. ~10–13) ≈ 385–500 USD/kWp @ 26k VNĐ/USD | DMT Solar bảng giá (06/2026); DHC Solar 12–16 tr (01/2026) cross-check | DMT Solar / DHC Solar | 2026-06-01 | — | 30/06/2026 | dmtsolar.com/dien-nang-luong-mat-troi | P8
B6 | Model | PV specific yield (HCMC, tilt 10°/az 180°/loss 14%) | ≈1,420 kWh/kWp/yr — FINALIZE via PVWatts run | NREL PVWatts; GSA + VietnamSolar HCMC 3.91 kWh/kWp·day (=1,427/yr) cross-check | NREL / World Bank GSA | 2026 | — | 30/06/2026 | globalsolaratlas.info | f2, f3-B6 (P8)
S8 | Standard | Rooftop PV self-consumption legal framework | <100 kW: notify; ≥100 kW: registration; post-FIT excess export ~no tariff | NĐ 135/2024/NĐ-CP; NĐ 58/2025/NĐ-CP | Chính phủ VN | 2024/2025 | — | 30/06/2026 | (gov/project file) | f2 (P8, P9)
EC5 | LCA (peer-rev.) | LFP battery embodied (cradle-to-gate, A1–A3 + B4) | 70 kgCO₂e/kWh (central); range 48–120 (sensitivity) | Degen et al. 2024, J. Cleaner Production (loc.-dependent LIB) | Degen et al. | 2024 | — | 30/06/2026 | doi:10.1016/j.jclepro.2024.142242 (sciencedirect S0959652624011739) | P9
EC-F6 | EC-Fallback | Battery embodied cross-check | 59–119 kgCO₂e/kWh (midpoint 89, utility-scale); 74–134 (datacenter LCA) | Forbes/Rapier 2020; Carbon Explorer (arXiv 2201.10036) | Forbes / Meta | 2020/2022 | — | 30/06/2026 | forbes.com/sites/rrapier (utility-scale battery) | cross-check P9
C7 | Cost | LFP BESS turnkey (battery+BMS, commercial 30–150 kWh) | 7–11 tr VNĐ/kWh ≈ 269–423 USD/kWh @ 26k; Pylontech 80tr/7kWh, Topband 13tr/kWh (resid.) → comm. lower | Suntech Solar 04/2026; VietnamSolar Stack100 05/2026 | Suntech / VietnamSolar | 04–05/2026 | — | 30/06/2026 | suntechsolar.vn/gia-thanh-pin-luu-tru ; vietnamsolar.vn | P9
B7 | Model | BESS dispatch model (rule-based) | Zero grid-charge, zero-export, pure PV self-consumption; RTE 90%; DoD 90%; 6000 cyc → 1 replacement/20y | Internal rule-based; LFP spec IEC 62619 (BYD/Pylontech) | internal / IEC | 2026 | — | 30/06/2026 | (project file) | f2, f3 (P9)
S9 | Standard/Tariff | EVN điện kinh doanh (Nhóm 3.3, 6–22kV) — cơ sở f2 avoided-cost | Trước VAT: BT 3.108 / TĐ 1.829 / CĐ 5.202 đ/kWh. Blended office (~70%BT/25%CĐ/5%TĐ) ≈3.568 đ = $0.137/kWh @26k. Sau VAT8% ≈3.853=$0.148. VAT recoverable→dùng before-VAT | QĐ 1279/QĐ-BCT (giá) + QĐ 963/QĐ-BCT (khung giờ) | Bộ Công Thương / EVN | 1279:09/05/2025; 963:22/04/2026 | — | 30/06/2026 | evn.com.vn ; evnspc.vn/TraCuu/ThongTinGiaDien | f2: P5/P6/P7 avoided + P8/P9 self-consumption
B8 | Model | DX gross↔net COP conversion (E+ table.htm DX Cooling Coils summary) | gross 3.3993 / net 2.96 / EER 10.09 / IEER 11.57; gross÷net=1.149; net COP=EER/3.412 | ASHRAE901_OfficeMedium_STD2019_HoChiMinh_table.htm | EnergyPlus |  |  | 30/06/2026 | (project file) | P5 (net↔gross basis)
S10 | Standard/Market | Packaged DX efficiency tiers (AHRI 340/360, ≥240k Btu/h, air-cooled) | 90.1-2019 ≥240k min EER~10.1 (L0); 90.1-2010 min EER 11.0/IEER 11.2; CEE Adv. Tier very-large ~13.5–14.5 IEER; AAON air-cooled EER 12.1–14.8 (2–240 ton) | AAON RTU page; E Source/Business Energy Advisor; ACEEE/CEE 2016 | AAON / E Source / ACEEE | 2016–2026 | — | 30/06/2026 | aaon.com/products/packaged-rooftop-units ; esource.bizenergyadvisor.com ; aceee.org | P5 ladder anchors
C8 | Cost | Packaged DX installed swap cost + efficiency premium | Full-unit swap ≈$2,000–2,800/ton installed (equip $1,000–1,400/ton large + install ≈ equal); base ≈$38–53/m²floor (93.5 ton ÷ 4982 m²); +~10–30% premium top tier; all-in RTU $14–28/SF context | thefurnaceoutlet 2025 (20-ton guide); Terrapin/RSMeans 2026 Q1 | The Furnace Outlet / Terrapin (RSMeans) | 2025–2026 | — | 30/06/2026 | thefurnaceoutlet.com ; terrapincg.com/news/commercial-hvac-cost-per-square-foot-2026 | P5 cost (US proxy; VN large-packaged-DX market thin)
EC7 | EPD-derived | IGU embodied A1–A3 (double low-e/SS, 6-12-6 tempered) | ≈30 kgCO₂e/m²glass (range 25–38) → 3.9 kgCO₂e/m²floor (×0.131); from flat glass 1102 kgCO₂e/ton + IGU fab/temper | Guardian NA flat glass EPD (2024) + EN 15804 IGU range | Guardian Glass / GSA | 2024 | — | 30/06/2026 | (EPD refs) | P4. AGC Thermobel 10-16-8 cross-check but EXPIRED 06/2024 → not cited for GWP
S11 | Standard/Product | Glazing property tiers (solar-control IGU, EN 410/673) | AGC solar-control range Ug 1.0–1.1, g 17–41%, Tv 24–74%; anchors Vitro Solarban 90 / Guardian SNX 51/23 (VT~0.51, SHGC~0.23) | AGC Thermobel EPD product table; Vitro/Guardian product data | AGC / Vitro / Guardian | 2019–2026 | — | 30/06/2026 | agc-yourglass.com ; vitrowindowglass.com | P4 ladder anchors
C9 | Cost | Low-E/solar-control IGU phôi (6-12-6 tempered) | 1,200,000–1,700,000 VNĐ/m² (std); tới 2,300,000 (nhập khẩu) = $46–88/m²glass @26k; +reglaze labor/edging ~40% → $8–19/m²floor (×0.131) | Havaco VN bảng giá Low-E 2026 | Havaco VN | 2026-03-04 | — | 30/06/2026 | havaco.vn/goc-tu-van/kinh-low-e-la-gi | P4 (panel; keep Al frame, WWR fixed)
B9 | Model | Glazing baseline & area (E+ IDF/table.htm) | U 2.862 / SHGC 0.219 / VT 0.241 (4 obj E/S/W/N); window area 652.62 m²; glass/floor=0.131; 13 Daylighting:Controls (VT→f1) | IDF SimpleGlazingSystem + table.htm fenestration | EnergyPlus / DOE | — | — | 30/06/2026 | (project file) | P4 baseline + normalization
C10 | Cost | Wall EPS ETICS installed (PROXY — VN market thin) | VN không có đơn giá ETICS sạch (panel tôn-xốp ≠ ETICS). Proxy: UK resid. £83–125/m²wall ($105–160); EU comm. ~$50–80; VN-adjusted ~$40–70/m²wall → ×0.266 = $10–20/m²floor | EWI Store UK (£8–12k/96m²); EU ETICS (Sika/Rockwool/Sto) | EWI Store / EU ETICS | 2024–2026 | — | 30/06/2026 | ewistore.co.uk/how-to-calculate-the-cost-of-an-external-wall-insulation-system | P1 (proxy; refine = báo giá nhà thầu facade VN; P1 expected inactive)
B10 | Model | Replacement (B4) COST model → f2 LCC engine | DX(P5) 1×@yr15 (ASHRAE RSL~15y)=C8 $/ton; PV inverter(P8) 1×@yr12=10–15%C6 ($40–75/kWp); BESS(P9) 1×@yr12 (6000cyc)=pack 65–75%C7 ($160–320/kWh). Price-decline bỏ qua=conservative. Discount→PV; KHÔNG vào Capital cost year-0 | Derived C6/C7/C8 + ASHRAE service life | internal / ASHRAE | 2026 | — | 30/06/2026 | (project file) | f2 (P5,P8,P9 replacement)
Note on H2: EN 15804 EPD hiệu lực 5 năm. Phát hành 2021 → có thể đã hết hạn. PHẢI verify trước submit; nếu hết hạn → tìm bản cập nhật hoặc dùng EC-F1 fallback + ghi Limitations.

## FixedParams
Parameter | Baseline value | Unit | Source | Note
Window-to-wall ratio (WWR) | 33 | % | B1 | Structural constraint (fixed)
Plug & process load density | 11.38 | W/m² | B1
Lighting power density (baseline) | 6.66 | W/m² | B1 | P7 ladder phải đi DƯỚI giá trị này
Occupant density | 18.58 | m²/person | B1 | Đồng nhất 15 zone (verified IDF)
HVAC system type | VAV (DX TwoSpeed) | – | B1 | Fixed → topology future work
Building conditioned floor area | 4982 | m² | B2 | A_floor normalization
Roof gross area | 1660.73 | m² | B2 | P2/P3 normalization
Glazing baseline U | 2.86 | W/m²·K | B1 | P4 (SimpleGlazingSystem)
Glazing baseline SHGC | 0.219 | – | B1 | P4 ladder phải ≤ 0.219 (đã rất thấp)
DX cooling COP (baseline, gross) | 3.40 | – | B1 | 3.39928881549157; tag 6 trường
Roof thermal emittance (TE, outer) | 0.75 | – | B2 | Giữ cố định cho P3 (single-variable); = ASHRAE 90.1 CZ0-3 min aged
Clothing insulation (occupied) | 0.5 | clo | B1 | PMV input (CLOTHING_SCH); cap trần P6
Indoor air velocity | 0.2 | m/s | B1 | PMV input (AIR_VELO_SCH); still air → P6 cap ~26°C; elevated-air = future work
Cooling setpoint setback (unoccupied) | 26.7 | °C | B1 | Giữ cố định; trần ladder P6 ≤ giá trị này

## Notes
# | Topic | Finding / action required | Affects | Status
1 | g2 sai threshold | QCVN roof = U≤1.00 W/m²K (R0≥1.00), KHÔNG phải 0.45. '0.45' nhặt nhầm từ bảng SHGC. → SỬA §3.6. | g2, §3.6 | OPEN
2 | g2 mái non-binding | Baseline roof R0=4.52 >> 1.00 → mọi level pass. Cân nhắc chuyển sang OTTVM≤25 W/m² (có solar, gắn cool-roof P3). | g2, §3.6, §3.7 | OPEN
3 | P1/P2 inactive (paradox) | Baseline vỏ đã ~R-25 → thêm cách nhiệt: operational saving nhỏ, embodied tăng → optimizer ưu tiên L0. Material cho NZEB Paradox. | §4 discussion | NOTE
4 | P5 = DX COP | Coil:Cooling:DX:TwoSpeed, KHÔNG phải chiller. COP ở 6 trường (3 coil × hi/lo) → jEPlus tag cả 6. Gross rated 3.39928881549157. | P5, §3.5 | NOTE
5 | EPD validity | EN 15804 hiệu lực 5 năm; ITB 148/2021 có thể hết hạn ~2026 → VERIFY trước submit. | EC1, Appendix D | OPEN
6 | EPS A1–A3 biến thiên | A1–A3 EPS chênh ~7× giữa các EPD theo quốc gia (Arslan 2024) → khóa 1 nguồn + nêu độ bất định Limitations. | f3, Limitations | NOTE
7 | P2 vật liệu = EPS (không XPS) | Lý do: (1) màng chống thấm nằm trên insulation → bảo vệ; (2) XPS A1–A3 chênh ~50× theo blowing agent, không công bố ở VN → không verify được. | P2 | DECIDED
8 | Chuẩn hóa | A1–A3 & cost chuẩn hóa /m² sàn (A_floor=4982). Roof factor = 1660.73/4982 = 0.333. | Inventory | NOTE
9 | P1 cost chưa chốt | P1 dùng chung EC1, nhưng giá EPS ETICS (tường) có thể khác board trần → cần dòng cost riêng (C-mới). | P1, DataSources | OPEN
10 | P3 baseline = code-min cool roof | SR 0.55 + TE 0.75 đúng bằng ASHRAE 90.1-2019 §5.5.3.1.1 (CZ0-3) → headroom hẹp; material cho NZEB Paradox | §4, P3 | NOTE
11 | P3 low-magnitude kỳ vọng | Mái đã R-25 + đã cool sẵn → P2×P3 substitutive; ΔEUI(P3) có thể chỉ đơn-vị-% | §4 discussion | NOTE
12 | P3 EC = ISO 21930 (không EN 15804) | EN 15804 chỉ có màng PU dày 2.3mm (sai FU); functional match > family; embodied P3 ≈0.03% operational → immaterial | EC2, Limitations | DECIDED
13 | P3 B4=0 + TE fixed | EPD FU=20y đã gộp recoat (RSL15y, Stage-3≈0) → B4=0 tránh double-count; TE giữ 0.75 = conservative (coating thật ~0.88) | P3, §3.6 | DECIDED
14 | P3 cost: KOVA marketing ≠ physics | phản xạ 90% = initial marketing, KHÔNG dùng cho E+; coverage datasheet chưa pin → cost band 1.7–2.7 | P3, C3 | OPEN
15 | P6 ladder cap 26°C | Setback 26.7 + comfort edge (0.5clo/0.2m·s⁻¹) ~26 → cap 26 tránh inversion & infeasible; improvement-only từ L0=24 | P6, §3.5 | DECIDED
16 | g1 thiếu PMV output | IDF có FANGER nhưng THIẾU Output:Variable "Zone Thermal Comfort Fanger Model PMV" → PHẢI thêm để jEPlus trích g1 | g1, jEPlus | OPEN
17 | P6 EMS optimum-start | CLGSETP có EMS actuator + schedule _STARTSTOP → tag occ value ở CẢ 2 schedule; verify EMS không override occupied SP | P6, jEPlus | OPEN
18 | P6 elevated air speed = future work | AIR_VELO_SCH fixed 0.2 m/s; nếu cho 0.8 m/s (quạt) setpoint có thể lên 27–28°C mà vẫn PMV≤0.5 | §future work | NOTE
19 | P7 LPD non-binding + free-win | QCVN 11 W/m² ≫ baseline 6.66 → non-binding. LED retrofit win-win: B6↓, embodied flat ~8.3, B4=0. Optimizer kỳ vọng pin floor L4=4.0. Contrast P1 paradox. | P7, §3.6, §4 | NOTE
20 | P7 EC/cost anchor N | N=0.18 đèn/m² chi phối EC & cost (±30%); embodied ~4% of 20y operational → không lật kết luận. Floor 4.0 = best-current panel efficacy ở độ rọi VP bảo toàn (≈0.37 W/ft²). | P7, Inventory, Limitations | NOTE
26 | Giá điện EVN chốt | Kinh doanh 3.3/6–22kV trước VAT: BT 3.108/TĐ 1.829/CĐ 5.202 (QĐ1279+963). f2 áp TOU theo giờ lên output E+; blended fallback 3.568 đ ($0.137). VAT8% recoverable→before-VAT | f2, S9 | DONE
27 | P1 cost = proxy | VN không có đơn giá ETICS sạch → proxy EU/UK $40–70/m²wall = $10–20/m²floor. Confidence THẤP; refine = báo giá nhà thầu. P1 expected inactive → low-stakes | P1, C10 | OPEN (proxy)
28 | B4-cost model | Thay thế DX@yr15 / inverter@yr12 / BESS@yr12 (B10) → LCC engine, không vào Capital cost year-0. Conservative (bỏ price-decline) | f2, B10 | DONE