## HO CHI MINH CITY
BUILDING SUMMARY
Item
Program
Building Prototype |  | Medium Office
Form
Building shape
Number of Floors |  | 3
Window Fraction (Window-to-Wall Ratio) |  | 33%
Architecture
Exterior walls Construction | Above-Grade Wall Type | Steel-Frame Walls (2X4 16IN OC) 0.4 in. Stucco+5/8 in. gypsum board + wall Insulation+5/8 in.
| Associated Space Conditioning Category | Nonresidential
Roof Constuction | Roof Type | Built-up roof: Roof membrane+roof insulation+metal decking
| Associated Space Conditioning Category | Nonresidential
CLIMATE ZONE
No | Country | Thermal Zone | Thermal Climate Zone Name | Representative City | Weather Location | Weather File Name
1 | International | 0A | Extremely Hot Humid | Ho Chi Minh City, Vietnam | Ho Chi Minh City/Tan Son Nhat Airport, Vietnam | VNM_Ho.Chi.Minh.City-Tan.Son.Nhat.AP.489000_IWEC2.epw
Zone and HVAC System Summary
Prototype Building | Prototype Building (raw_data) | Thermal Zone | Area [ft2] | Multipliers | Conditioned | HVAC System Type (90.1-2004) | HVAC System Name | Gross Wall Area [ft2] | Window Glass Area [ft2] | Space Type for LPD | Occupancy Category | Lighting Power Desnity [W/ft2] | Design Occupancy Density [people/1,000 ft2] | Electric Equipment [W/ft2] | Gas Equipment [W/ft2] | Total OSA Ventilation [cfm/ft2] |  |  | Exhaust Airflow [cfm/ft2] | Envelope Infiltration (Flow/Exterior Wall Area) [cfm/ft2] | Envelope Infiltration (Flow/Zone) [cfm/zone] | Infiltration Through Entrances [cfm/zone]
[12 empty] | 90.1-2004 |  |  |  | 90.1-2004 (62-1999) cfm/per | 90.1-2004 (62-1999) cfm/sf | 90.1-2004 (62-1999) cfm/zone
Medium Office
Medium Office | OfficeMedium | CORE_BOTTOM | 10586.7262 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_BOT | 0 | 0 | Weighted | Office space | 1.0244 | 5.0002 | 2.326 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Medium Office | OfficeMedium | TOPFLOOR_PLENUM | 17875.9316 | 1 | Yes | NA |  | 2183.3495 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | MIDFLOOR_PLENUM | 17875.9316 | 1 | Yes | NA |  | 2183.3495 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | FIRSTFLOOR_PLENUM | 17875.9316 | 1 | Yes | NA |  | 2183.3495 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | CORE_MID | 10586.7262 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_MID | 0 | 0 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Medium Office | OfficeMedium | CORE_TOP | 10586.7262 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_TOP | 0 | 0 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_TOP_ZN_3 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_TOP | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_TOP_ZN_2 | 1412.8695 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_TOP | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74968 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_TOP_ZN_1 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_TOP | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_TOP_ZN_4 | 1412.7619 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_TOP | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_BOT_ZN_3 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_BOT | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_BOT_ZN_2 | 1412.8695 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_BOT | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74968 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_BOT_ZN_1 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_BOT | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 2209.9979
Medium Office | OfficeMedium | PERIMETER_BOT_ZN_4 | 1412.7619 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_BOT | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_MID_ZN_3 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_MID | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_MID_ZN_2 | 1412.8695 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_MID | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74968 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_MID_ZN_1 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_MID | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_MID_ZN_4 | 1412.7619 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_MID | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | Total | 53627.7949 |  |  |  |  | 14737.5013 | 7024.7364 |  |  | 1.0244 | 5.0002 | 1.0609
Medium Office | OfficeMedium | Conditioned Total | 53627.7949 |  |  |  |  | 14737.5013 | 7024.7364 |  |  | 1.0244 | 5.0002 | 1.0609
Medium Office | OfficeMedium | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Fenestration_Weights
| Type 1 |  | Type 2 |  |  | Type 3
Building Prototype | Fixed | Operable | Nonmetal | Metal - Fixed | Metal - Operable | Nonmetal | Curtain wall / Storefront | Metal - all other
Medium Office | 96.88% | 3.117% | 2.475% | 95.75% | 1.777% | 2.475% | 64.84% | 32.69%
Schedule Summary
Prototype | Schedule | Space Type | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | 12 pm | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 am
OfficeMedium | Lighting | All | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Lighting | All | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Electric Equipment | All | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
OfficeMedium | Electric Equipment | All | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeMedium | Electric Equipment | All | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeMedium | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeMedium | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
OfficeMedium | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0
OfficeMedium | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
OfficeMedium | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Infiltration | All | Sun | bar: 1 am to 12 am
OfficeMedium | Cooling Set Point | All | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | Cooling Set Point | All | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | Cooling Set Point | All | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | Heating Set Point | All | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium | Heating Set Point | All | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | Heating Set Point | All | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
HVAC System Type Dictionary
Source: ASHRAE Standard 90.1-2019 Table G3.1.1-4
System No. | System Type | Fan Control | Cooling Type (a) | 1 am: Heating Type (a)
1. PTAC | Packaged terminal air conditioner | Constant volume | Direct expansion | 1 am: Hot-water fossil fuel boiler
2. PTHP | Packaged terminal heat pump | Constant volume | Direct expansion | 1 am: Electric heat pump
3. PSZ-AC | Packaged rooftop air conditioner | Constant volume | Direct expansion | 1 am: Fossil fuel furnace
4. PSZ-HP | Packaged rooftop heat pump | Constant volume | Direct expansion | 1 am: Electric heat pump
5. Packaged VAV with reheat | Packaged rooftop VAV with reheat | VAV | Direct expansion | 1 am: Hot-water fossil fuel boiler
6. Packaged VAV with PFP boxes | Packaged rooftop VAV with parallel fan power boxes and reheat | VAV | Direct expansion | 1 am: Electric resistance
7. VAV with reheat | VAV with reheat | VAV | Chilled water | 1 am: Hot-water fossil fuel boiler
8. VAV with PFP boxes | VAV with parallel fan-powered boxes and reheat | VAV | Chilled water | 1 am: Electric resistance
9. Heating and ventilation | Warm air furnace, gas fired | Constant volume | None | 1 am: Fossil fuel furnace
10. Heating and ventilation | Warm air furnace, electric | Constant volume | None | 1 am: Electric resistance
11. SZ–VAV | Single-zone VAV | VAV | Chilled water | 1 am: See note (b).
12. SZ-CV-HW | Single-zone system | Constant volume | Chilled water | 1 am: Hot-water fossil fuel boiler
13. SZ-CV-ER | Single-zone system | Constant volume | Chilled water | 1 am: Electric resistance
14. WSHP (CRAC) | Water source heat pump (Computer room air conditioning unit) | Constant volume | Fluid cooler | 1 am: Hot-water fossil fuel boiler
15. WSHP | Water source heat pump | Constant volume | Fluid cooler | 1 am: Gas boiler
1.1 PTAC with electric heating | Packaged terminal air conditioner with electric heating | Constant volume | Direct expansion | 1 am: Electric resistance
3.1 PSZ-AC-Two-speed-fan | Packaged rooftop air conditioner with two speed fan | Two-speed | Direct expansion | 1 am: Fossil fuel furnace
3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant)
4.1 PSZ-HP-Two-speed-fan | Packaged rooftop heat pump with two speed fan | Two-speed | Direct expansion | 1 am: Electric heat pump
4.2 PSZ-HP with gas auxiliary heat | Packaged rooftop heat pump with gas auxiliary heat | Constant volume | Direct expansion | 1 am: Electric heat pump
4. PSZ-HP or 4.1 PSZ-HP-Two-speed-fan (size dependant)
5.1 Packaged VAV with gas central heating and electric reheat | Packaged rooftop VAV with gas central heating and electric reheat | VAV | Direct expansion | 1 am: Gas central heating and electric reheat
5.2 Packaged VAV with electric central heating and electric reheat | Packaged rooftop VAV with electric central heating and electric reheat | VAV | Direct expansion | 1 am: Electric central heating and electric reheat
7.1 VAV with electric central heating and electric reheat | VAV with electric central heating and electric reheat | VAV | Chilled water | 1 am: Electric resistance
7.2 VAV with hydronic central heating and electric reheat | VAV with hydronic central heating and electric reheat | VAV | Chilled water | 1 am: Hot-water fossil fuel boiler for central heating and electric resistance for reheat
11.1 SZ–VAV with hydronic heating | Single-zone VAV | VAV | Chilled water | 1 am: Hot-water fossil fuel boiler
11.2 SZ–VAV with electric heating | Single-zone VAV | VAV | Chilled water | 1 am: Electric resistance
15.1 WSHP with electric boiler | Water source heat pump with electric boiler | Constant volume | Fluid cooler | 1 am: Electric boiler
16. Four-pipe fan-coil | Four-pipe fan-coil | Constant volume | Chilled water | 1 am: Hot-water fossil fuel boiler
16.1 Four-pipe fan-coil with DOAS | Four-pipe fan-coil with DOAS | Constant volume | Chilled water | 1 am: Hot-water fossil fuel boiler
15.2 WSHP with MZ DOAS | Water source heat pump for conditioning, central DOAS for ventilation with ERV without DCV?
4.3 PSZ-HP with DOAS | Packaged rooftop heat pump with DOAS | Constant volume? | Direct expansion | 1 am: Electric heat pump
No heating and cooling
ideal loads
a. For purchased chilled water and purchased heat, see G3.1.1.3.
b. For Climate Zones 0 through 3A, the heating type shall be electric resistance. For all other climate zones the heating type shall be hot-water fossil-fuel boiler.